## Executive_Summary
FRM April 2026 - BESS Financial Analysis Summary
Generated: 2026-02-07 10:37
SCENARIO OVERVIEW
Scenario | Voltage | Power | Energy | Duration | Primary Value
A: The Urban Modular | 4.0 kV | 0.5 MW | 2.0 MWh | 4.0 hr | Phase Balancing + Resiliency
B: The Feeder Relief | 12.0 kV | 2.5 MW | 10.0 MWh | 4.0 hr | Peak Shaving + Deferral
C: The Sub-Transmission | 34.5 kV | 10.0 MW | 40.0 MWh | 4.0 hr | Capacity Injection + Arbitrage
KEY FINANCIAL METRICS BY SCENARIO & COST VARIATION
Metric | Scenario A |  | Scenario B |  | Scenario C
| Turnkey | Equip Only | Turnkey | Equip Only | Turnkey | Equip Only
Total CapEx | 700000 | 527700 | 3500000 | 2638500 | 14000000 | 10554000
Net CapEx (after ITC) | 490000 | 369390 | 2450000 | 1846950 | 9800000 | 7387800
NPV | 649615.226 | 790015.3759 | 2984432.899 | 3686433.649 | 10883158.6731 | 13691161.6728
BCR | 1.9419 | 2.4382 | 1.8654 | 2.3422 | 1.789 | 2.2463
IRR | 21.32% | 29.25% | 20.25% | 27.87% | 19.17% | 26.49%
Payback (years) | 4.6204 | 3.4115 | 4.8474 | 3.576 | 5.0975 | 3.7572
LCOS ($/MWh) | 125.0732 | 99.6121 | 125.0732 | 99.6121 | 125.0732 | 99.6121
Year 1 Revenue | 127000 | 127000 | 610000 | 610000 | 2340000 | 2340000
Year 1 Costs | 21460.25 | 18961.9 | 107301.25 | 94809.5 | 429205 | 379238
KEY ASSUMPTIONS
Discount Rate (WACC) | 7.0%
Analysis Period | 20 years
ITC Rate | 30%
Round-Trip Efficiency | 85%
Annual Degradation | 2.5%
Cycles per Day | 1.0
Turnkey Cost | $350/kWh
Equipment Only Cost | $220/kWh

## Scenario_A
Scenario A: The Urban Modular
Small-scale urban deployment for critical load support and distribution phase balancing
TECHNICAL SPECIFICATIONS
Voltage Class | 4.0 kV
Power Rating | 0.5 MW (500 kW)
Energy Capacity | 2.0 MWh (2,000 kWh)
Duration | 4.0 hours
Primary Value Stream | Phase Balancing + Resiliency
CAPITAL COST COMPARISON
Component | Turnkey | Equipment Only
Equipment/Base Cost | 700000 | 440000
Installation | 0 | 40000
Commissioning | 0 | 12500
Engineering | 0 | 35200
Total CapEx | 700000 | 527700
ITC Credit | -210000 | -158310
Net CapEx | 490000 | 369390
Cost per kWh | 350 | 263.85
Cost per kW | 1400 | 1055.4
ANNUAL VALUE STACK (YEAR 1)
Revenue Stream | $/kW-year | Annual Value
T&D Deferral | 45 | 22500
Energy Arbitrage | 20 | 10000
Resource Adequacy | 144 | 72000
Ancillary Services | 12 | 6000
Voltage Support | 8 | 4000
Resiliency Premium | 25 | 12500
TOTAL | 254 | 127000
FINANCIAL METRICS COMPARISON
Metric | Turnkey | Equipment Only
Net Present Value | 649615.226 | 790015.3759
Benefit-Cost Ratio | 1.9419 | 2.4382
Internal Rate of Return | 21.32% | 29.25%
Payback Period (years) | 4.6204 | 3.4115
LCOS ($/MWh) | 125.0732 | 99.6121
PV of Benefits | 1339307.6123 | 1339307.6123
PV of Costs | 689692.3863 | 549292.2364

## Scenario_B
Scenario B: The Feeder Relief
Mid-scale feeder deployment for peak load management and T&D deferral
TECHNICAL SPECIFICATIONS
Voltage Class | 12.0 kV
Power Rating | 2.5 MW (2,500 kW)
Energy Capacity | 10.0 MWh (10,000 kWh)
Duration | 4.0 hours
Primary Value Stream | Peak Shaving + Deferral
CAPITAL COST COMPARISON
Component | Turnkey | Equipment Only
Equipment/Base Cost | 3500000 | 2200000
Installation | 0 | 200000
Commissioning | 0 | 62500
Engineering | 0 | 176000
Total CapEx | 3500000 | 2638500
ITC Credit | -1050000 | -791550
Net CapEx | 2450000 | 1846950
Cost per kWh | 350 | 263.85
Cost per kW | 1400 | 1055.4
ANNUAL VALUE STACK (YEAR 1)
Revenue Stream | $/kW-year | Annual Value
T&D Deferral | 45 | 112500
Energy Arbitrage | 35 | 87500
Resource Adequacy | 144 | 360000
Ancillary Services | 12 | 30000
Voltage Support | 8 | 20000
Resiliency Premium | 0 | 0
TOTAL | 244 | 610000
FINANCIAL METRICS COMPARISON
Metric | Turnkey | Equipment Only
Net Present Value | 2984432.899 | 3686433.649
Benefit-Cost Ratio | 1.8654 | 2.3422
Internal Rate of Return | 20.25% | 27.87%
Payback Period (years) | 4.8474 | 3.576
LCOS ($/MWh) | 125.0732 | 99.6121
PV of Benefits | 6432894.8307 | 6432894.8307
PV of Costs | 3448461.9317 | 2746461.1818

## Scenario_C
Scenario C: The Sub-Transmission
Large-scale sub-transmission deployment for capacity and energy market participation
TECHNICAL SPECIFICATIONS
Voltage Class | 34.5 kV
Power Rating | 10.0 MW (10,000 kW)
Energy Capacity | 40.0 MWh (40,000 kWh)
Duration | 4.0 hours
Primary Value Stream | Capacity Injection + Arbitrage
CAPITAL COST COMPARISON
Component | Turnkey | Equipment Only
Equipment/Base Cost | 14000000 | 8800000
Installation | 0 | 800000
Commissioning | 0 | 250000
Engineering | 0 | 704000
Total CapEx | 14000000 | 10554000
ITC Credit | -4200000 | -3166200
Net CapEx | 9800000 | 7387800
Cost per kWh | 350 | 263.85
Cost per kW | 1400 | 1055.4
ANNUAL VALUE STACK (YEAR 1)
Revenue Stream | $/kW-year | Annual Value
T&D Deferral | 15 | 150000
Energy Arbitrage | 55 | 550000
Resource Adequacy | 144 | 1440000
Ancillary Services | 12 | 120000
Voltage Support | 8 | 80000
Resiliency Premium | 0 | 0
TOTAL | 234 | 2340000
FINANCIAL METRICS COMPARISON
Metric | Turnkey | Equipment Only
Net Present Value | 10883158.6731 | 13691161.6728
Benefit-Cost Ratio | 1.789 | 2.2463
Internal Rate of Return | 19.17% | 26.49%
Payback Period (years) | 5.0975 | 3.7572
LCOS ($/MWh) | 125.0732 | 99.6121
PV of Benefits | 24677006.3998 | 24677006.3998
PV of Costs | 13793847.7268 | 10985844.7271

## Cash_Flows
Annual Cash Flow Analysis - All Scenarios
Scenario A - Turnkey (EPC Included)
Year | Costs | Benefits | Net CF | Cumulative
0 | 490000 | 0 | -490000 | -490000
1 | 21460.25 | 127000 | 105539.75 | -384460.25
2 | 21102.4938 | 126920.625 | 105818.1313 | -278642.1188
3 | 20744.9314 | 126841.2996 | 106096.3682 | -172545.7505
4 | 20387.5581 | 126762.0238 | 106374.4657 | -66171.2849
5 | 20030.3692 | 126682.7975 | 106652.4284 | 40481.1435
6 | 19673.3599 | 126603.6208 | 106930.2608 | 147411.4043
7 | 19316.5259 | 126524.4935 | 107207.9676 | 254619.3719
8 | 18959.8628 | 126445.4157 | 107485.5529 | 362104.9248
9 | 18603.3662 | 126366.3873 | 107763.0211 | 469867.9459
10 | 18247.0321 | 126287.4083 | 108040.3763 | 577908.3222
20 | 14691.7783 | 125500.3282 | 110808.5499 | 688716.8721
Scenario A - Equipment Only
Year | Costs | Benefits | Net CF | Cumulative
0 | 369390 | 0 | -369390 | -369390
1 | 18961.9 | 127000 | 108038.1 | -261351.9
2 | 18690.2938 | 126920.625 | 108230.3313 | -153121.5688
3 | 18418.8814 | 126841.2996 | 108422.4182 | -44699.1505
4 | 18147.6581 | 126762.0238 | 108614.3657 | 63915.2151
5 | 17876.6192 | 126682.7975 | 108806.1784 | 172721.3935
6 | 17605.7599 | 126603.6208 | 108997.8608 | 281719.2543
7 | 17335.0759 | 126524.4935 | 109189.4176 | 390908.6719
8 | 17064.5628 | 126445.4157 | 109380.8529 | 500289.5248
9 | 16794.2162 | 126366.3873 | 109572.1711 | 609861.6959
10 | 16524.0321 | 126287.4083 | 109763.3763 | 719625.0722
20 | 13830.2783 | 125500.3282 | 111670.0499 | 831295.1221
Scenario B - Turnkey (EPC Included)
Year | Costs | Benefits | Net CF | Cumulative
0 | 2450000 | 0 | -2450000 | -2450000
1 | 107301.25 | 610000 | 502698.75 | -1947301.25
2 | 105512.4688 | 609618.75 | 504106.2812 | -1443194.9688
3 | 103724.657 | 609237.7383 | 505513.0812 | -937681.8875
4 | 101937.7906 | 608856.9647 | 506919.1741 | -430762.7134
5 | 100151.8458 | 608476.4291 | 508324.5833 | 77561.8698
6 | 98366.7997 | 608096.1313 | 509729.3316 | 587291.2015
7 | 96582.6297 | 607716.0712 | 511133.4415 | 1098424.643
8 | 94799.314 | 607336.2487 | 512536.9347 | 1610961.5777
9 | 93016.8311 | 606956.6635 | 513939.8324 | 2124901.4102
10 | 91235.1603 | 606577.3156 | 515342.1553 | 2640243.5655
20 | 73458.8916 | 602796.8521 | 529337.9606 | 3169581.5261
Scenario B - Equipment Only
Year | Costs | Benefits | Net CF | Cumulative
0 | 1846950 | 0 | -1846950 | -1846950
1 | 94809.5 | 610000 | 515190.5 | -1331759.5
2 | 93451.4688 | 609618.75 | 516167.2812 | -815592.2188
3 | 92094.407 | 609237.7383 | 517143.3312 | -298448.8875
4 | 90738.2906 | 608856.9647 | 518118.6741 | 219669.7866
5 | 89383.0958 | 608476.4291 | 519093.3333 | 738763.1198
6 | 88028.7997 | 608096.1313 | 520067.3316 | 1258830.4515
7 | 86675.3797 | 607716.0712 | 521040.6915 | 1779871.143
8 | 85322.814 | 607336.2487 | 522013.4347 | 2301884.5777
9 | 83971.0811 | 606956.6635 | 522985.5824 | 2824870.1602
10 | 82620.1603 | 606577.3156 | 523957.1553 | 3348827.3155
20 | 69151.3916 | 602796.8521 | 533645.4606 | 3882472.7761
Scenario C - Turnkey (EPC Included)
Year | Costs | Benefits | Net CF | Cumulative
0 | 9800000 | 0 | -9800000 | -9800000
1 | 429205 | 2340000 | 1910795 | -7889205
2 | 422049.875 | 2338537.5 | 1916487.625 | -5972717.375
3 | 414898.6281 | 2337075.9141 | 1922177.2859 | -4050540.0891
4 | 407751.1624 | 2335615.2416 | 1927864.0792 | -2122676.0099
5 | 400607.3834 | 2334155.4821 | 1933548.0987 | -189127.9111
6 | 393467.1988 | 2332696.6349 | 1939229.4361 | 1750101.525
7 | 386330.5188 | 2331238.6995 | 1944908.1807 | 3695009.7057
8 | 379197.2558 | 2329781.6753 | 1950584.4195 | 5645594.1252
9 | 372067.3244 | 2328325.5618 | 1956258.2373 | 7601852.3625
10 | 364940.6413 | 2326870.3583 | 1961929.717 | 9563782.0795
20 | 293835.5662 | 2312368.2525 | 2018532.6863 | 11582314.7658
Scenario C - Equipment Only
Year | Costs | Benefits | Net CF | Cumulative
0 | 7387800 | 0 | -7387800 | -7387800
1 | 379238 | 2340000 | 1960762 | -5427038
2 | 373805.875 | 2338537.5 | 1964731.625 | -3462306.375
3 | 368377.6281 | 2337075.9141 | 1968698.2859 | -1493608.0891
4 | 362953.1624 | 2335615.2416 | 1972662.0792 | 479053.9901
5 | 357532.3834 | 2334155.4821 | 1976623.0987 | 2455677.0889
6 | 352115.1988 | 2332696.6349 | 1980581.4361 | 4436258.525
7 | 346701.5188 | 2331238.6995 | 1984537.1807 | 6420795.7057
8 | 341291.2558 | 2329781.6753 | 1988490.4195 | 8409286.1252
9 | 335884.3244 | 2328325.5618 | 1992441.2373 | 10401727.3625
10 | 330480.6413 | 2326870.3583 | 1996389.717 | 12398117.0795
20 | 276605.5662 | 2312368.2525 | 2035762.6863 | 14433879.7658

## Value_Stack
Value Stack Components & Assumptions
BASE VALUE ASSUMPTIONS ($/kW-year)
Component | Low | Medium | High
T&D Deferral | 15 | 30 | 45
Energy Arbitrage | 20 | 35 | 55
Resource Adequacy | $12/kW-mo | 0
Ancillary Services | 12
Voltage Support | 8
Resiliency Premium | 25 | (Scenario A only)
SCENARIO VALUE TIER ASSIGNMENTS
Scenario | Deferral Tier | Arbitrage Tier | Resiliency
A: The Urban Modular | High | Low | Yes
B: The Feeder Relief | High | Medium | No
C: The Sub-Transmission | Low | High | No

## Cost_Inputs
Cost Input Assumptions
COST VARIATION COMPARISON
Parameter | Turnkey | Equipment Only
Base Equipment ($/kWh) | 350 | 220
Installation ($/kW) | Included | 80
Commissioning ($/kW) | Included | 25
Engineering (%) | Included | 8%
Includes EPC | Yes | No
ITC Eligible | Yes | Yes
OPERATING COST ASSUMPTIONS
Fixed O&M | $22/kW-year
Variable O&M | $0.5/MWh
Insurance | 0.5% of CapEx
Property Tax | 1.0% of asset value
FINANCIAL PARAMETERS
Discount Rate (WACC) | 7.0%
Analysis Period | 20 years
ITC Base Rate | 30%
Domestic Content Adder | 10% (if applicable)
Inflation Rate | 2.5%
TECHNICAL PARAMETERS
Round-Trip Efficiency | 85%
Annual Degradation | 2.5%
Cycles per Day | 1.0
Duration | 4 hours (all scenarios)