## Inputs
BESS Economic Analyzer — JIT Cohort Model
Version 2.0 ¦ February 2026 ¦ For Electric Utility Engineering & Finance
ASSUMPTION LIBRARY
Selected Library | NREL ATB 2024 - Moderate Scenario | ↑ Overrides defaults below |  | Options: NREL ATB 2024 - Moderate Scenario ¦ Lazard LCOS v10.0 - 2025 ¦ CPUC California 2024
PROJECT BASICS
Project Name | My BESS Project |  |  | Descriptive project name
Project ID | BESS-001 |  |  | Unique identifier for tracking
Location / Market | CAISO NP15 |  |  | ISO zone or substation name
Total Capacity (MW) | 0 |  |  | Auto-summed from Build Schedule
Duration (hours) | 4 |  |  | 1–8 hrs typical utility-scale
Total Energy (MWh) | 0 |  |  | Auto-calculated
Analysis Period (years) | 20 |  |  | 15–25 yrs typical
Discount Rate (WACC) | 7% |  |  | 6–10% utility; 8–12% merchant
Ownership Type | Utility |  |  | "Utility" or "Merchant"
PHASED BUILD SCHEDULE (JIT Cohort Model)
Notes / Description | COD Year | Capacity (MW) | ITC Rate (%)
| 2027 | 20 | 0%
| 2028 | 20 | 0%
| 2029 | 20 | 0%
| 2030 | 20 | 0%
| 2031 | 20 | 0%
| 2032 | 0 | 0%
| 0 | 0 | 0%
| 0 | 0 | 0%
| 0 | 0 | 0%
| 0 | 0 | 0%
T&D CAPITAL DEFERRAL ¦ PV = K × [1 − ((1+g)/(1+r))^n] (up to 10 independent projects)
Tranche | Notes / Description | Capital Cost K ($) | Deferral Yrs (n) | Growth Rate g (%) | PV ($)
Project 1 |  | 100000000 | 5 | 2% | 0
Project 2 |  | 0 | 5 | 2% | 0
Project 3 |  | 0 | 5 | 2% | 0
Project 4 |  | 0 | 5 | 2% | 0
Project 5 |  | 0 | 5 | 2% | 0
Project 6 |  | 0 | 5 | 2% | 0
Project 7 |  | 0 | 5 | 2% | 0
Project 8 |  | 0 | 5 | 2% | 0
Project 9 |  | 0 | 5 | 2% | 0
Project 10 |  | 0 | 5 | 2% | 0
TOTAL T&D DEFERRAL PV |  |  |  |  | 0
TECHNOLOGY SPECIFICATIONS
Battery Chemistry | LFP |  |  | LFP (default) ¦ NMC ¦ Other
Round-Trip Efficiency (RTE) | 85% |  |  | AC-AC efficiency including inverter losses (70–95%)
Annual Degradation Rate | 2.5% |  |  | Capacity loss per year; 2.5% typical for LFP
Cycle Life (full cycles) | 6000 |  |  | Number of full-depth cycles before end-of-life
Augmentation Year | 12 |  |  | Year battery modules are replaced; typically 10–12
Cycles per Day | 1 |  |  | Average daily full charge-discharge cycles (0.1–3.0)
COST INPUTS — BESS
CapEx ($/kWh) | 160 |  |  | $130–200/kWh utility-scale LFP
Fixed O&M ($/kW-year) | 25 |  |  | Site maintenance, monitoring, security
Variable O&M ($/MWh) | 0 |  |  | Per-MWh discharge cost; often $0 for LFP
Augmentation Cost ($/kWh) | 55 |  |  | Battery module replacement; learning-curve adjusted
Decommissioning ($/kW) | 10 |  |  | End-of-life removal and site restoration
Charging Cost ($/MWh) | 30 |  |  | Grid electricity cost for charging cycles
Residual Value (% of CapEx) | 10% |  |  | Salvage value at end of analysis period
INVESTMENT TAX CREDIT — BESS-Specific (IRA 2022)
ITC Base Rate | 30% |  |  | 30% base rate for standalone storage under IRA
ITC Adders | 0% |  |  | Energy community +10%, Domestic content +10%, Low-income +10–20%
INFRASTRUCTURE COSTS — Common to All Utility Projects
Interconnection ($/kW) | 100 |  |  | Network upgrades, studies, metering
Land ($/kW) | 10 |  |  | Site acquisition or capitalized lease
Permitting ($/kW) | 15 |  |  | Environmental review, permits, legal
Insurance (% of CapEx) | 0.5% |  |  | Annual property & liability insurance
Property Tax (% of book) | 1% |  |  | Annual property tax on net book value
FINANCING STRUCTURE (overrides Discount Rate for WACC)
Debt Financing (%) | 60% |  |  | 60% debt / 40% equity typical utility
Interest Rate on Debt | 4.5% |  |  | Annual debt interest rate
Loan Term (years) | 15 |  |  | Amortization period
Cost of Equity | 10% |  |  | Required equity return
Corporate Tax Rate | 21% |  |  | 21% federal; add state if applicable
Calculated WACC | 0% |  |  | WACC = (E/V)×Re + (D/V)×Rd×(1-Tc) — use this as Discount Rate
ANNUAL BENEFIT STREAMS ($/kW-year, Year 1)
Benefit Name | $/kW-yr (Y1) | Escalation/yr | Category | Source
Resource Adequacy | 150 | 2% | Common | CPUC RA Program D.24-06-050
Energy Arbitrage | 40 | 2% | Common | CAISO OASIS historical LMPs
Ancillary Services | 15 | 1% | Common | CAISO AS market data
T&D Deferral | 25 | 1.5% | Common | CPUC Avoided Cost Calculator
Resilience Value | 50 | 2% | Common | LBNL ICE Calculator
Renewable Integration | 25 | 2.5% | BESS-Specific | CAISO Curtailment Reports
GHG Emissions Value | 15 | 3% | BESS-Specific | EPA Social Cost of Carbon
Voltage Support | 10 | 1% | Common | EPRI Distribution Studies
COST PROJECTIONS — Technology Learning Curve
Annual Cost Decline Rate | 12% |  |  | 12% per NREL ATB 2024 — applied to augmentation & multi-tranche CapEx
Cost Base Year | 2024 |  |  | Reference year for base CapEx and augmentation costs

## Calculations
CALCULATION ENGINE — Cohort-Based SUMPRODUCT Formulas
COHORT-BASED COST AGGREGATION
Total Capacity (kW) | 0 | Sum of all online cohort capacities in kW
Total Energy (kWh) | 0 | Total energy capacity kWh
Total Battery CapEx ($) | 0 | Cohort CapEx with learning-curve adjustment by COD year
Total ITC Credit ($) | 0 | ITC credit per cohort based on its learning-curve-adjusted CapEx
Net Year-0 Battery Cost ($) | 0 | Total CapEx minus ITC (before infrastructure costs)
Infrastructure Costs ($) | 0 | Interconnection + land + permitting (one-time, Year 0)
Total Net Year-0 Cost ($) | 0 | Battery net cost + infrastructure
Annual Fixed O&M ($) | 0 | Fixed O&M when all tranches are online
Annual Charging Cost ($) | 0 | Annual electricity cost for charging (all tranches online)
Annual Insurance ($) | 0 | Insurance = total CapEx × insurance rate
Augmentation Cost (Year {aug_yr}) ($) | 0 | Augmentation adjusted for learning curve

## Cash_Flows
Annual Cash Flow Projections — Cohort-Aggregated
Year | CapEx (net ITC) | Fixed O&M | Charging | Augment | Infra | Total Costs | PV Costs | Total Benefits | PV Benefits | Net CF | PV Net CF | Cumul CF | Energy (MWh)
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTALS / PV SUM | [6 empty] | 0 |  | 0 |  | 0 |  | 0

## Results
BESS Economic Analysis — Results Dashboard
Project: [auto from Inputs!C9] ¦ Analysis Date: February 20, 2026
KEY FINANCIAL METRICS
Metric | Value | Benchmark | Interpretation
Net Present Value (NPV) | 0 | > $0 | Positive NPV creates shareholder/ratepayer value
T&D Deferral PV | 0 | — | Present value of deferred T&D capital investment
Total Project Value | 0 | > $0 | NPV inclusive of T&D deferral benefit
Benefit-Cost Ratio (BCR) | 0 | ≥ 1.0 approve | ≥1.5 strong ¦ 1.0–1.5 marginal ¦ <1.0 reject (CPUC SPM)
Internal Rate of Return (IRR) | 0% | > WACC | IRR > WACC creates value above cost of capital
Simple Payback (years) | 0 | < 10 yrs | < 7 yrs strong; 7–10 acceptable; > 10 yrs challenging
LCOS ($/MWh) | 0 | $100–200/MWh | Levelized cost per MWh discharged (Lazard methodology)
Breakeven CapEx ($/kWh) | 0 | > CapEx input | Max CapEx where BCR = 1.0 (margin of safety)
PROJECT SUMMARY
Project Name | 0
Capacity (MW) | 0
Duration (hrs) | 0
Analysis Period | 0
Discount Rate | 0
WACC (Financing) | 0
Ownership Type | 0
CapEx ($/kWh) | 0
ITC Rate | 0

## Sensitivity
SENSITIVITY ANALYSIS — Tornado Chart Parameters
Each row shows the base case and ±20% deviation for one input parameter. Recalculate NPV in Python GUI for exact values; Excel shows analytical estimates.
PARAMETER SENSITIVITY TABLE
Parameter | Low Case | Base Case | High Case | Low NPV (est.) | Base NPV | High NPV (est.)
CapEx ($/kWh) | Inputs!C53 × 0.80 (−20% CapEx) | 0 | Inputs!C53 × 1.20 (+20% CapEx) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Discount Rate | Inputs!C16 × 0.80 (−20% rate) | 0 | Inputs!C16 × 1.20 (+20% rate) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Resource Adequacy ($/kW-yr) | Inputs!C79 × 0.75 (−25% RA) | 0 | Inputs!C79 × 1.25 (+25% RA) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Learning Rate | Inputs!C88 × 0.42 (5% rate) | 0 | Inputs!C88 × 1.25 (15% rate) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Round-Trip Efficiency | Inputs!C47 × 0.90 (−10% RTE) | 0 | Inputs!C47 × 1.05 (+5% RTE) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Analysis Period (yrs) | Inputs!C15 × 0.80 (−20% years) | 0 | Inputs!C15 × 1.20 (+20% years) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
ITC Rate | Inputs!C61 × 0.67 (No adders) | 0 | Inputs!C61 × 1.00 (+10% adder) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
Fixed O&M ($/kW-yr) | Inputs!C54 × 0.80 (−20% O&M) | 0 | Inputs!C54 × 1.20 (+20% O&M) | ← run Python GUI for exact | 0 | ← run Python GUI for exact
HOW TO READ A TORNADO CHART
• Parameters are sorted by impact (longest bar = highest sensitivity)
• Bars extending left (negative) show parameters where increase hurts NPV
• CapEx and Discount Rate typically dominate BESS sensitivity
• RA value is the largest single benefit driver in capacity-constrained markets
• Use the Python GUI → Sensitivity tab for exact recalculations and chart export
RECOMMENDED SCENARIO RANGES
Parameter | Low | Base | High | Source
CapEx ($/kWh) | $130 | $160 | $200 | NREL ATB 2024
Discount Rate | 6.0% | 7.0% | 9.0% | CPUC authorized WACC range
Resource Adequacy | $120/kW | $150/kW | $200/kW | CPUC RA decisions
Learning Rate | 5% | 12% | 15% | BNEF / NREL ATB
Degradation Rate | 1.5% | 2.5% | 3.5% | Manufacturer data
Analysis Period (yrs) | 15 | 20 | 25 | Utility planning horizon

## UOS_Analysis
UTILITY-OWNED STORAGE (UOS) — Revenue Requirement Analysis
Per CPUC D.25-12-003 (SCE 2026-2028 Cost of Capital) ¦ Populate from Python GUI or override below.
COST OF CAPITAL (D.25-12-003 SCE Defaults)
Parameter | Value | Default | Notes
Return on Equity (ROE) | 10.03% | 10.03% | Per D.25-12-003
Cost of Debt | 4.71% | 4.71%
Cost of Preferred | 5.48% | 5.48%
Equity Ratio | 52% | 52.00%
Debt Ratio | 43.47% | 43.47%
Preferred Ratio | 4.53% | 4.53%
Authorized ROR | 7.59% | 7.59% | Composite: T_state + T_fed×(1-T_state)
Federal Tax Rate | 21% | 21.00%
State Tax Rate (CA) | 8.84% | 8.84%
Property Tax Rate | 1% | 1.00%
RATE BASE INPUTS
Parameter | Value |  | Notes
Book Life (years) | 20 |  | Straight-line depreciation life
MACRS Property Class | 7 |  | 7-year MACRS for utility storage
Bonus Depreciation (%) | 0 |  | IRA bonus depreciation if applicable
Gross Plant (from Inputs) | 0 |  | Battery CapEx + infrastructure
ITC Amount | 0 |  | ITC applied to battery CapEx only
Annual O&M | 0 |  | Fixed O&M from Inputs sheet
REVENUE REQUIREMENT SCHEDULE (populate via Python GUI)
Year | Gross Plant | Book Depr | Tax Depr (MACRS) | ADIT | Net Rate Base | Return on RB | Income Tax | Property Tax | O&M | Revenue Req.
1 | — | — | — | — | — | — | — | — | — | —
2 | — | — | — | — | — | — | — | — | — | —
3 | — | — | — | — | — | — | — | — | — | —
4 | — | — | — | — | — | — | — | — | — | —
5 | — | — | — | — | — | — | — | — | — | —
6 | — | — | — | — | — | — | — | — | — | —
7 | — | — | — | — | — | — | — | — | — | —
8 | — | — | — | — | — | — | — | — | — | —
9 | — | — | — | — | — | — | — | — | — | —
10 | — | — | — | — | — | — | — | — | — | —
11 | — | — | — | — | — | — | — | — | — | —
12 | — | — | — | — | — | — | — | — | — | —
13 | — | — | — | — | — | — | — | — | — | —
14 | — | — | — | — | — | — | — | — | — | —
15 | — | — | — | — | — | — | — | — | — | —
16 | — | — | — | — | — | — | — | — | — | —
17 | — | — | — | — | — | — | — | — | — | —
18 | — | — | — | — | — | — | — | — | — | —
19 | — | — | — | — | — | — | — | — | — | —
20 | — | — | — | — | — | — | — | — | — | —
WIRES vs. NON-WIRES ALTERNATIVE (NWA) COMPARISON
Traditional Wires Cost ($/kW) | 500 |  | Cost per kW of traditional T&D infrastructure upgrade
Wires Book Life (years) | 40
Wires Lead Time (years) | 5
NWA Deferral Years | 5
NWA Incrementality Adjustment | Yes |  | Apply incrementality adjustment per CPUC NWA framework
SLICE-OF-DAY (SOD) FEASIBILITY
Min Qualifying Hours (SOD) | 4 |  | Minimum hours of discharge to qualify for RA (typically 4h)
Deration Threshold | 50% |  | Minimum capacity factor to maintain SOD qualification
SOD Feasibility Result | ← Run Python GUI for SOD check

## Library_Data
ASSUMPTION LIBRARIES — Comparison of NREL ¦ Lazard ¦ CPUC
Source data embedded from JSON libraries. Select a library on the Inputs sheet to auto-apply.
LIBRARY OVERVIEW
Parameter | NREL ATB 2024 Moderate | Lazard LCOS v10.0 (2025) | CPUC California 2024 | Guidance
VERSION
Version | 2024.2 | 10.1 | 2024.2
Published | 2024-04-15 | 2025-03-01 | 2024-11-01
Source | NREL ATB | Lazard LCOS | CPUC/E3 ACC
TECHNOLOGY
Chemistry | LFP | LFP | LFP
Round-Trip Eff. | 85% | 86% | 85% | AC-AC incl inverter
Annual Degradation | 2.5% | 2.0% | 2.5% | Capacity fade per year
Cycle Life | 6,000 | 6,500 | 6,000 | Full cycles before EOL
Augmentation Year | 12 | 12 | 12 | Battery module replacement yr
Cycles per Day | 1.0 | 1.0 | 1.0
COSTS ($/kWh unless noted)
CapEx ($/kWh) | $160 | $145 | $155 | Installed 4-hr LFP system
Fixed O&M ($/kW-yr) | $25 | $22 | $26 | Site O&M, monitoring
Variable O&M ($/MWh) | $0 | $0.50 | $0 | Per-MWh cost
Augmentation ($/kWh) | $55 | $50 | $52 | Battery replacement cost
Decommissioning ($/kW) | $10 | $8 | $12 | End-of-life removal
Charging Cost ($/MWh) | $30 | $35 | $25 | Grid electricity for charging
Residual Value | 10% | 10% | 10% | % of CapEx at end
INFRASTRUCTURE COSTS
Interconnection ($/kW) | $100 | $90 | $120 | Network upgrades, metering
Land ($/kW) | $10 | $8 | $15 | Site acquisition/lease
Permitting ($/kW) | $15 | $12 | $20 | Env review, permits
Insurance (% CapEx) | 0.5% | 0.5% | 0.5% | Annual insurance
Property Tax | 1.0% | 1.0% | 1.05% | CA average 1.05%
TAX CREDITS
ITC Base Rate | 30% | 30% | 30% | IRA base rate
ITC Adders | 0% | 0% | 10% | Energy community (CA common)
Total ITC | 30% | 30% | 40%
BENEFIT STREAMS ($/kW-year, Year 1)
Resource Adequacy | $150 | $140 | $180 | CA premium; CPUC D.24-06-050
Energy Arbitrage | $40 | $45 | $35 | CAISO OASIS historical
Ancillary Services | $15 | $12 | $10 | Frequency reg, spinning res
T&D Deferral | $20 | $20 | $25 | CPUC Avoided Cost Calc
Resilience Value | $40 | $45 | $60 | LBNL ICE; CA PSPS premium
Renewable Integration | $20 | $20 | $30 | CAISO curtailment value
GHG Emissions Value | $15 | $12 | $20 | CARB cap-and-trade
Voltage Support | $10 | $6 | $10 | Distribution services
COST PROJECTIONS
Learning Rate | 12% | 10% | 11% | Annual cost decline
Base Year | 2024 | 2025 | 2024
FINANCING (typical)
Debt Percent | 60% | 65% | 65%
Interest Rate | 4.5% | 5.0% | 4.0%
Cost of Equity | 10.0% | 10.0% | 9.5%
Tax Rate | 21% | 21% | 21%

## Methodology
METHODOLOGY — Formulas, Citations, and Assumptions
All calculations follow CPUC Standard Practice Manual and cited industry sources.
FINANCIAL METRICS
Net Present Value (NPV) | NPV = Σ CFt / (1+r)^t for t=0..N CF0 = −CapEx + ITC; CFt = Benefits(t) − O&M(t) − Charging(t) − Insurance(t) − PropertyTax(t) Source: Brealey, Myers & Allen, Principles of Corporate Finance, 13th ed. McGraw-Hill 2020, Ch.2
Benefit-Cost Ratio (BCR) | BCR = PV(Benefits) / PV(Costs) BCR ≥ 1.5 → Approve ¦ 1.0–1.5 → Further Study ¦ < 1.0 → Reject Source: CPUC Standard Practice Manual, Economic Analysis of Demand-Side Programs, 2001
Internal Rate of Return (IRR) | IRR = r such that NPV = 0 (solved numerically via Newton-Raphson / Excel IRR()) Source: Brealey et al., Ch.5
Levelized Cost of Storage (LCOS) | LCOS = PV(Lifetime Costs) / PV(Lifetime Energy Discharged) [$/MWh] Costs include CapEx, O&M, charging, augmentation; Energy = MWh discharged per year × RTE Source: Lazard Levelized Cost of Storage Analysis v10.0, 2025
Simple Payback | Payback = first year t where Cumulative Net CF ≥ 0 (linear interpolation within year) Not time-value adjusted; use as secondary screening metric only
Breakeven CapEx | BE_CapEx = (PV_Benefits − PV_OpEx) / Total_Capacity_kWh [$/kWh] Maximum CapEx where BCR = 1.0; safety margin = BE_CapEx − actual CapEx
COST STRUCTURE
Year 0 Capital Costs | Battery CapEx = CapEx($/kWh) × capacity(kWh) × (1 − LearningRate)^(COD − BaseYear) Infrastructure = (Interconnection + Land + Permitting)($/kW) × capacity(kW) ITC credit = Battery CapEx × (ITC_base + ITC_adders) [applied to battery only]
Annual Operating Costs | Fixed O&M = FOM($/kW-yr) × capacity(kW) Variable O&M = VOM($/MWh) × annual_discharge(MWh) Charging = charging_cost($/MWh) × annual_charge(MWh) Insurance = insurance_rate × total_CapEx Property Tax = property_tax_rate × net_book_value(t)
Augmentation | Occurs at augmentation_year; cost adjusted for learning curve: Aug_Cost(t) = base_aug_cost × (1 − learning_rate)^t Restores capacity to nominal; subsequent degradation resets
Battery Degradation | Capacity(t) = Capacity(0) × (1 − degradation_rate)^t Applied to energy-based benefits and LCOS energy denominator Source: NREL ATB 2024; manufacturer data
MULTI-TRANCHE (JIT) METHODOLOGY
Cohort-Based Cost Aggregation | Each tranche i has its own COD year t_i and capacity q_i. CapEx_i = q_i(kWh) × c_0 × (1−λ)^(t_i − t_base) where λ = learning rate Costs and benefits are summed across all online cohorts each year.
Staged Degradation | Each cohort degrades from its own COD: Capacity_i(t) = q_i × (1 − d)^(t − t_i) for t > t_i Benefits scale by effective online capacity / total nominal capacity
Flexibility Value | FV = PV(Upfront Build) − PV(Phased JIT Build) Positive FV shows economic advantage of deferring capital and capturing learning curve Computed in Python engine; displayed in Results tab of GUI
BENEFIT METHODOLOGIES
Resource Adequacy | Value = RA_capacity_credit($/kW-yr) × online_MW × 1000 Capacity credit uses ELCC methodology per CPUC rules Source: CPUC RA Program, D.24-06-050, November 2024
T&D Capital Deferral | PV = K × [1 − ((1+g)/(1+r))^n] K = deferred capital cost; g = load growth; r = discount rate; n = deferral years Source: E3 CPUC Avoided Cost Calculator 2024
GHG Emissions Value | Value = displaced_emissions(tCO2) × carbon_price($/tCO2) Carbon price per EPA Social Cost of Carbon / CARB cap-and-trade Source: EPA Technical Support Document — Social Cost of Greenhouse Gases, 2023
REFERENCES
Primary Data Sources | 1. NREL Annual Technology Baseline 2024 — atb.nrel.gov/electricity/2024 2. Lazard LCOS Analysis v10.0, 2025 — lazard.com 3. CPUC Standard Practice Manual — cpuc.ca.gov 4. E3 Avoided Cost Calculator 2024 — cpuc.ca.gov/acc 5. LBNL ICE Calculator — icecalculator.com
Regulatory References | 6. CPUC D.24-06-050 — Resource Adequacy 2024 7. CPUC D.25-12-003 — SCE 2026-2028 Cost of Capital 8. FERC Order 841 — Electric Storage Market Participation 9. IRS Notice 2023 — IRA Investment Tax Credit Guidance
Academic / Industry | 10. Brealey, Myers & Allen — Principles of Corporate Finance, 13th ed. 11. NREL Storage Futures Study — NREL/TP-6A20-77449 12. EPRI Grid Energy Storage — Technical Report 3002020045 13. BloombergNEF Battery Price Survey 2025

## VBA_Instructions
VBA MACRO GUIDE — Embedded Buttons and Functions
This workbook includes VBA macros for report generation and data export. Enable macros when prompted. Requires .xlsm format.
ENABLING MACROS
Required for full functionality | When opening the file, click "Enable Content" in the yellow security bar. If macros are blocked by IT policy, use the Python GUI instead (python main.py).
Macro Security Setting | File → Options → Trust Center → Trust Center Settings → Macro Settings Select "Disable all macros with notification" for safe operation.
AVAILABLE MACRO BUTTONS
Calculate Project Economics | Runs the Python calculation engine via Shell() command. Reads all Inputs sheet values and writes results to Results, Cash_Flows sheets. Button location: Results sheet, top-right
Export PDF Report | Exports Results + Cash_Flows + Sensitivity to a formatted PDF. Output saved to same folder as workbook with timestamp in filename. Button location: Results sheet
Load Library Assumptions | Reads the selected library (Inputs!C6) and populates cost/tech/benefit fields. Overrides any manually entered values in the yellow input cells. Button location: Inputs sheet, row 6
Clear All Inputs | Resets all yellow input cells to default values from the selected library. Does NOT clear library selection or project name/ID. Button location: Inputs sheet, top
Generate Sensitivity Chart | Runs 8 sensitivity scenarios via Python and creates a tornado chart. Chart saved to Sensitivity sheet. Button location: Sensitivity sheet
Export to JSON | Saves all current inputs to a .json project file for use in the Python GUI. Enables round-trip compatibility between Excel and Python interfaces. Button location: Inputs sheet
USING WITHOUT MACROS
Manual Workflow | 1. Enter project parameters in yellow cells on the Inputs sheet 2. Cash_Flows and Results sheets update automatically via Excel formulas 3. Run python main.py for IRR, LCOS, Payback exact calculations 4. Copy Python results back to Results sheet manually
Python GUI | Launch: cd bess_analyzer && python main.py Full feature set: JIT cohort model, UOS analysis, sensitivity, PDF export Save projects as JSON; load back into GUI or regenerate Excel from command line
Regenerating This File | Run: python excel_generator.py (from bess_analyzer/ directory) Output: BESS_Analyzer_v2.0_YYYYMMDD_HHMM.xlsx with current timestamp All formulas and sheet structure are rebuilt from source code
KEYBOARD SHORTCUTS
Recalculate | F9 — force full workbook recalculation
Navigate sheets | Ctrl+PgUp / Ctrl+PgDn — move between sheets
Find named range | Ctrl+G → type range name (e.g., Build_Schedule) → Enter
Freeze panes | View → Freeze Panes on any sheet for easier scrolling